## Slide 1
Resource Adequacy: Current Practice and Game Changers
Work in progress
Chanan Singh
Texas A&M University

## Slide 2: Capacity Adequacy Planning in PJM
One occurrence in ten year is the basis for determining PJM’s required Installed Reserve Margin (IRM).
The generation adequacy standard PJM is based on Section 1 of the ReliabilityFirst Reliability Principles and Standards2,

## Slide 3: Capacity Adequacy Planning in PJM
“Sufficient megawatt generating capacity shall be installed to ensure that in each year for the ReliabilityFirst system the probability of occurrence of load exceeding the available generating capacity shall not be greater, on the average, than one day in ten years. Among the factors to be considered in the calculation of the probability are the characteristics of the loads, the probability of error in load forecast, the scheduled maintenance requirements for generating units, the forced outage rates of generating units, limited energy capacity, the effects of connections to other pools, and network transfer capabilities within the ReliabilityFirst systems.”
Copied from ReliabilityFirst

## Slide 4: Capacity Adequacy Planning in PJM*
The criterion 1 in 10 applied uniformly across the entire PJM region regardless of NERC reliability council boundaries.
The Reserve Requirement Study is performed annually by Resource Adequacy Department at PJM with extensive stakeholder review through the PJM Committee structure.
The IRM ultimately recommended by the Committees and approved by the PJM Board.
Notes: Capacity Adequacy is now Resource Adequacy Department. Use more recent presentations.

## Slide 5: Capacity Adequacy Planning in PJM
Approval by the Board is based on consideration of the analytical results and application of engineering judgment to reflect the influence of factors not explicitly considered in the analysis.
PRISM (Probabilistic Reliability Index Study Model) is the computer application used by PJM to calculate reliability indices to determine installed capacity reserve requirements.

## Slide 6: RESOURCE ADEQUACY PLANNING IN NE-ISO
For Forward Capacity Market (FCM), ISO New England Inc. (ISO-NE) conducts a Forward Capacity Auction (FCA) three years in advance of each Capacity Commitment Period (CCP).
The ICR is the minimum level of capacity required to meet the reliability requirements.
Notes: PJM also has a capacity market (RPM) 3 years in advance of the Delivery Year. Started in 2005 (my work while at PJM).

## Slide 7: Reliability Standards for New England Area Bulk Power Supply
“Resources will be planned and installed in such a manner that, after due allowance for the factors enumerated below, the probability of disconnecting non-interruptible customers due to resource deficiency, on the average, will be no more than once in ten years. Compliance with this criterion shall be evaluated probabilistically, such that the loss of load expectation (LOLE) of disconnecting non-interruptible customers due to resource deficiencies shall be, on average, no more than 0.1 day per year.”

## Slide 8: Power System Reliability Indices
Traditionally LOLE, also called LOLE daily is calculated based on daily peak loads only, ie, it is number of days on which peak was not satisfied.
It has been extended by some utilities as the number of days on which load was not satisfied any hour of the day.
LOLE hourly measures the number of loss of load hours per year.
Neither measures the depth of loss of load which can be measured by Expected Energy not Served.
Frequency and duration indices have also been proposed.
However, currently LOLE daily appears to be the index predominantly used by ISOs such as NYISO,PJM and ISO-NE.
Notes: It is ISO-NE, not NEISO.

## Slide 9: Game Changers
Variable Energy Resources – wind and solar.
Storage
Demand Flexibility options
DERs at the Distribution level
DERs behind the meter
Energy vs Capacity Planning
Notes: VERs include some types of hydro also. What is the last bullet as Game Changer?

## Slide 10: Variable Energy Resources – wind and solar.
Traditionally, except for the energy limited units, the capacity is derated or unavailable because of partial or full failure of the unit.
With wind or solar, the unit may be perfectly healthy but capacity may not be available because of wind speed or solar insolation.
Although there may be sufficient energy generated by these units, the capacity may not be available when needed for load balancing.
Storage and demand flexibility may provide solution to this problem.
Given a large penetration of such resources, can capacity-based resource adequacy planning work?

## Slide 11: Demand Flexibility
To a certain extent demand can be modified to fit the generation available.
It can be either response to incentives or made by network
What is the meaning of resource adequacy when demand can be modified to suit to the capacity available?
How to you define ‘loss of load’ in the context of demand flexibility?
What is the meaning of a target LOLE in the presence of demand flexibility?

## Slide 12: DERs at the Distribution Level
Traditionally resource adequacy has been performed at the Generation and Transmission level or bulk power systems.
Distribution systems have been assumed to be the passive consumers of electricity.
How do DERs at the distribution level, participating in demand, change the resource adequacy planning?

## Slide 13: DERs behind the meter
Ultimately the reliability experienced by the customer is what is important.
With solar and storage behind the meter, customer participates in reliability it receives.
Adequacy planning at the ISO level may have less impact on the customer with DERs behind the meter.
How does this customer participation in reliability improvement impacts the adequacy planning at the ISO level?
Notes: See my notes on Slide 12. DERs operating continuously can reduce the load or DERs start when dispatched. Two ways of contribution to adequacy.

## Slide 14: Indices and how to use them
Is LOLE meaningful with variable energy resources and demand flexibility?
Does the traditional resource adequacy planning based on a target LOLE need to be revisited?
With DERs at the distribution level and behind the meter, who is responsible for reliability?
Notes: DERs and Demand Flexibility can vary hourly so LOLE hourly index may be more desirable that LOLE daily. ISO is responsible for Adequacy related load drop. Distribution company is responsible for load drop due to distribution component failure. Another issue: If DERs are used as system resources and get capacity revenues they should be used for the system (cannot isolate from the system and serve the local load).

## Slide 15: Tools
With DERs and demand flexibility, sequential Monte Carlo, in principle, appears to be the logical tool for reliability evaluation?
Are there adequate commercial tools available for this purpose?
Notes: Modeling hundreds of small DERs each with its own operating rules in a bulk power system reliability tool may be impractical.

## Slide 16: Miscellaneous
With distribution and edge actively participating in reliability assurance, do the jurisdictions of entities like NERC need to be revisited?
There is NERC GAD data for traditional adequacy planning. There is need to data collection on DERs.
How would distribution level participation and partial defection from grid impact resource availability at Grid level and ultimately impact reliability?